## 49T
RATINGS:
Temperature - Maximum operating temperature 625 F (329 C).
Electrical Rating -
| Type 49T - | 8 amp noninductive at 250 v ac.
7.2 amp noninductive at 277 v ac.
10 FLA, 60 LRA at 120 v ac.
5 FLA, 30 LRA at 240 v ac.
125 va pilot duty at 120 and 240 v ac.
Note - Type 49T has also been tested as a safety control (100,000 cy) for electrical ratings of 25 amp noninductive at 250 v ac and 15 amp noninductive at 277 v ac. At these over 2000 va ratings the controls may be used only for application where the spacings as specified in the Construction Details section are acceptable.
Type 49TX - 25 amp noninductive at 250 v ac.
15 amp noninductive, at 277 v ac.
10 FLA, 60 LRA,at 120 v ac.
5 FLA, 30 LRA at 240 v ac.
125 va pilot duty at 120 and 240 v ac.