## 60T
Models | Volts( AC) | FLA, (A) | LRA, (A) | VA, pilot duty | A, res | Other | Manual Reset or action, type and cycles | Automatic Action, type and Cycles (@11) | Function, Temp. Cut-off or Limit (@12)
60T-(@1) | 24 (DC) | -- | -- | -- | 5 | -- | -- | 2.B, 100k | Cut-out
| 120 | 10 | 60 | 125 | 25 | 15A, GP | -- | 2.B, 100k | Cut-out
| 240 | 5 | 30 | 125 | 25 | -- | -- | 2.B, 100k | Cut-out
| 250 @1 | 10 | 60 | -- | -- | -- | -- | 2.B, 30k | Limiter
| 277 | -- | -- | 125 | 21.6 | -- | -- | 2.C, 100k | Limiter
60T-(@2) | 120 | 10 | 60 | 125 | 25 | 15A, GP | -- | 2.B, 100k | Cut-out
| 240 | 5 | 30 | 125 | 25 | -- | -- | 2.B, 100k | Cut-out
| 250 @7 | 10 | 60 | -- | -- | -- | -- | 2.B, 30k | Limiter
| 277 | -- | -- | 125 | 21.6 | -- | -- | 2.C, 100k | Limiter
60T-(@3) | 120 | 10 | 60 | 125 | 25 | -- | -- | 2.B, 100k | Cut-out
60TE-(@3)
Contacts 1 and 3 only | 240 | 5 | 30 | 125 | 25 | -- | -- | 2.B, 100k | Cut-out
| 277 | -- | -- | 125 | 21.6 | -- | -- | 2.C, 100k | Limiter
60T-(@8) | 120 | -- | -- | 125 | -- | -- | -- | 2.B, 100k | Cut-Out
60TE-(@8)
60TX-(@8)
60TXE-(@8) | 120 @7 | 5.8 | 34.8 | -- | 10 | -- | -- | 2.C, 6k | Limiter
60TXX-(@8) | 240 | -- | -- | 125 | -- | -- | -- | 2.B, 100k | Cut-Out
60TXXE-(@8) | 240 @7 | 2.9 | 17.4 | -- | 10 | -- | -- | 2.C, 6k | Limiter
Contacts 1 and 2 only | 277 | -- | -- | 125 | -- | -- | -- | 2.C, 100k | Limiter
60T-(@5) | 120 | -- | -- | -- | 15 | 8.33 A, 1000W Tungsten | 2.B.J, 6k | -- | Cut-out
60TX-(@5)
60TXX-(@5)
| 277 | -- | -- | -- | 25 | -- | 2.C.J, 6k | -- | Limiter
@9 | 480 | 0.65 | 3.9 | 125 | 12.5 | -- | 2.C.J, 6k | -- | Limiter
| 480 | 5.5 | 33 | 1061 | -- | -- | 2.C.J, 6k | -- | Limiter
| 600 | 2 | 12 | 400 | 10 | -- | 2.C.J, 6k | -- | Limiter
60TX-(@1) | 120 | 10 | 60 | 125 | 25 | 15 amp, GP | -- | 2.B, 100k | Cut-out
60TXX-(@1) | 240 | 5 | 30 | 125 | 25 | -- | -- | 2.B, 100k | Cut-out
| 250 @1 | 10 | 60 | -- | -- | -- | -- | 2.B, 30k | Limiter
| 277 | -- | -- | 125 | 21.6 | -- | -- | 2.C, 100k | Limiter
| 480 @2 | -- | -- | 125 | 12.5 | -- | -- | 2.C, 100k | Limiter
| 600 | 2 | 12 | 400 | 10 | -- | -- | 2.C, 100k | Limiter
File E19279 | Vol. 1 | Sec. 37 | Page 3 | Issued: 2012-04-02
| and Report | Revised: 2018-07-31
60TX-(@2) | 120 | 10 | 60 | 125 | 25 | 15 amp, GP | -- | 2.B, 100k | Cut-out
60TXX-(@2) | 240 | 5 | 30 | 125 | 25 | -- | -- | 2.B, 100k | Cut-out
| 250 @7 | 10 | 60 | -- | -- | -- | -- | 2.B, 30k | Limiter
| 277 | -- | -- | 125 | 21.6 | -- | -- | 2.C, 100k | Limiter
| 480 @2 | -- | -- | 125 | 12.5 | -- | -- | 2.C, 100k | Limiter
| 600 | 2 | 12 | 400 | 10 | -- | -- | 2.C, 100k | Limiter
60TX-(@3) | 120 | 10 | 60 | 125 | 25 | -- | -- | 2.B, 100k | Cut-out
60TXX-(@3)
60TEX-(@3) | 240 | 5 | 30 | 125 | 25 | -- | -- | 2.B, 100k | Cut-out
60TEXX-(@3) | 277 | -- | -- | 125 | 21.6 | -- | -- | 2.C, 100k | Limiter
Contacts 1 and 3 only | 480 @2 | -- | -- | 125 | 12.5 | -- | -- | 2.C, 100k | Limiter
60TX-(@5) | 120 | -- | -- | -- | 25 | 8.33 A, 1000W Tungsten | 2.B.J, 6k | -- | Cut-out
60TXX-(@5)
| 277 | -- | -- | -- | 25 | -- | 2.B.J, 6k | -- | Cut-out
| 480 | 0.65 | 3.9 | 125 | 12.5 | -- | 2.C.J, 6k | -- | Limiter
| 480 | 5.5 | 33 | 1061 | -- | -- | 2.C.J, 6k | -- | Limiter
60TG-(@1) | 6 to 24 | -- | -- | 4 | -- | 3 Watts, resistive | -- | 2.B, 100k | Cut-out
60TG-(@2 ) | 6 to 24 DC | -- | -- | 1 | -- | -- | -- | 2.B, 100k | Cut-out
| 1 to 24 DC | -- | -- | -- | -- | 1 Watt, resistive | -- | 2.B, 100k | Cut-out
60TV-(@6 ) | 120 | 2.6 | 15.5 | 125 | -- | -- | 2.B.J, 6k | -- | Cut-out
| 12 DC | - | - | - | 0.1 | - |  | - | Cut-out
60T with suffix J @10 | 0-50 | -- | -- | -- | -- | -- | -- | -- | --
69T-(@1) | 120 | 10 | 60 | 125 | 25 | 15A, 0.8PF | -- | 1.C, 100k | Limiter
69TK-(@1)
69T-(@2)
69TK(@2)
| 240 | 5 | 30 | 125 | 25 | -- | -- | 1.C, 100k | Limiter
| 277 | -- | -- | 125 | 21.6 | -- | -- | 1.C, 100k | Limiter
69T-(@3) | 120 | 10 | 60 | 125 | 25 | -- | -- | 1.C, 100k | Limiter
69TK-(@3)
| 240 | 5 | 30 | 125 | 25 | -- | -- | 1.C, 100k | Limiter
Contacts 1 and 3 only | 277 | -- | -- | 125 | 21.6 | -- | -- | 1.C, 100k | Limiter
69T-(@8) | 120 |  |  | 125 |  | -- | -- | 1.C, 100k | Limiter
69TK-(@8)
Contacts 1 and 2 only

## 60T_MH5304
Temperature - Fixed setting not to exceed 350 F (177 C).
Range, Degrees F Differential
70-180 10 F minimum
70-200 15 F minimum
80-200 25 F minimum
205-250 24 F minimum
255-300 24 F minimum
100-200 35 F minimum, 55 F maximum
200-250 34 F minimum, 66 F maximum
255-300 33 F minimum, 77 F maximum
305-350 42 F minimum, 88 F maximum
Electrical -
*
60TXX
| VOLTAGE | 120Vac |  | 240Vac |  | 250Vac
| DEVICE | SPST | SPDT | SPST | SPDT | SPST
LOAD | CYCLES
Pilot Duty | 100000 | 480 | -- | 480 | -- | --
(VA) |  | -- | 125 | -- | 125 | --
Motor | 100000 | 1960-10-01 | -- | 2025-05-30 | -- | --
(FLA/LRA) | 30000 | 14/72 | 5.8/34.8 | 10/60 | 2.9/17.4 | 10/60
Resistive | 100000 | 25 | -- | 25 | -- | --
(A) | 30000 | -- | -- | -- | -- | --
| 6000 | -- | 10 | -- | 10 | --
60T Manual Reset M2 |  | 2nd suffix 5
| VOLTAGE | 120Vac | 277Vac | 480Vac
| CONTACTS | SPST | SPST | SPST
LOAD | CYCLES
Pilot Duty | 6000 | -- | -- | 1061
Motor | 6000 | -- | -- | 5.5/33
Resistive | 6000 | -- | 25 | 12.5
Tungsten | 6000 | 1000W | -- | --
61F Single Operation
| VOLTAGE | 120Vac | 240Vac | 277Vac | 480Vac | 600Vac
| CONTACTS | SPST | SPST | SPST | SPST | SPST
LOAD | CYCLES
Pilot Duty | 1 | 1000 | 1000 | 1000 | 1000 | 1000
Motor | 1 | 14/72 | 14/72 | -- | -- | --
Resistive | 1 | 48 | 49 | 48 | 48 | 48
61FA Single Operation
| VOLTAGE | 120Vac | 240Vac
| CONTACTS | SPST | SPST
LOAD | CYCLES
Pilot Duty | 1 | 1000 | 1000
Motor | 1 | 12/72 | 12/72
Resistive | 1 | 48 | 49
*
File MH5304 | Vol. 2 | Sec. 3 | Page 2-2 | Issued: 1959-07-22
| and Report | Revised: 2010-06-09
60F Single Operation
| VOLTAGE | 120Vac | 240Vac | 277Vac | 480Vac | 600Vac
| CONTACTS | SPST | SPST | SPST | SPST | SPST
LOAD | CYCLES
Pilot Duty | 1 | 500 | 500 | 500 | 500 | 500
Motor | 1 | 14/72 | 14/72 | -- | -- | --
Resistive | 1 | 25 | 25 | 25 | 25 | 25
60TV?5, where ? is 0,1,2,4,8
| VOLTAGE | 120Vac
| CONTACTS | SPST
LOAD | CYCLES
Pilot Duty | 6000 | 125
Motor | 6000 | 2.6/15.5