## 64T_MH5304
RATINGS:
TEMPERATURE
* Maximum operating and ambient temperature, 350°F.
ELECTRICAL
Type 64T, Suffixes -01, -11, -21 and -41
Two loads, same or opposite polarity ratings are given per pole. Load terminals - lower or upper switch.
Rating - 2000 W noninductive, 240 through 300 V ac; 10 FLA, 60 LRA, 120 V ac; 5 FLA, 30 LRA, 240 V ac; 2.5 FLA, 15 LRA, 300 V ac; 480 VA, 120 through 300 V ac pilot duty.
Types 64TX and 64TXX, Suffixes -01, -11, -21 and -41
Two loads, same or opposite polarity ratings are given per pole. Load terminals - lower or upper switch.
Rating - 6000 W noninductive, 240 through 300 V ac; 10 FLA, 60 LRA, 120 V ac; 5 FLA, 30 LRA, 240 V ac; 2.5 FLA, 15 LRA, 300 V ac; 480 VA, 120 through 300 V ac pilot duty.
Note: The above Types 64T, 64TX and 64TXX controls have been tested 100,000 c separately for each pole at opposite polarity for electrical ratings of 6000 W maximum, 2.5 FLA, 15 LRA and 480 VA pilot duty at voltages up to 480 V ac. At this rating the control may be used where the electrical spacings as indicated under "Construction Details" would conform with
requirements.
File MH5304 | Vol. 8 | Sec. 1 | Page 3 | Issued: 1977-05-10
| and Report | Revised: 1985-12-05
Type 64T, Suffixes -02, -12, -22 and -42
Two loads, same or opposite polarity ratings are given per pole. Load terminals - lower and upper switch.
Rating - 2000 W, 240 through 300 V ac resistive; 10 FLA, 60 LRA, 120 V ac; 5 FLA, 30 LRA, 240 V ac; 2.5 RLA, 15 LRA, 300 V ac; 480 VA, 120 through 300 V ac pilot duty.
Types 64TX and 64TXX, Suffixes -20, -12, -22 and -42
Rating - 6000 W, 240 through 300 V ac resistive; 10 FLA, 60 LRA, 120 V ac; 5 FLA, 30 LRA, 240 V ac; 2.5 FLA, 15 LRA, 300 V ac; 480 VA, 120 through 300 V ac pilot duty.
Note: The above Types 64T, 64TX and 64TXX controls have been tested 100,000 c separately for each pole at opposite polarity for electrical ratings of 6000 W noninductive, 240 through 480 V ac, 2.5 FLA, 15 LRA at 480 V ac, 480 VA pilot duty at 120 through 480 V ac. At these ratings the control may be used in applications where the electrical spacings as indicated under "Construction Details" would conform with requirements.

## 64F_E19279
Series | Contact Description | Volt. VAC, | Electrical Ratings |  |  | Opening Temp | Operating or Protective | Complete Declar.
|  |  | Current, Amps (+) | Number of cycles | Type of Load | Rating, °C |  | (i.e. 1.C.L, etc.)
All 64F | Load 1 (terminals 2-4); NC | 600 V ac, 60 Hz | 40 A | 1 | Resistive | 140°F-300°F, | Protective | 2.B
reset temperature:
≤-35°C
| Load 2 (terminals 1-3); NC | 600 V ac, 60 Hz | 40 A | 1 | Resistive